TYPE SKY-1M SLIDING SMOKE VENTILATOR SPECIFICATION

I. 		PART ONE - GENERAL

1.01		SUMMARY

A.	Work included: Furnishing and installing factory fabricated smoke ventilator ( vent)

B.	Related Work: [Insert applicable specifications sections]

1.02		REFERENCES

BS EN 12101-2

Construction Product Regulation  No. 305/2011

1.03		SUBMITTALS

A.	Product Data: Provide manufacturer’s product data for all materials in this specification.

B.	Shop Drawings: Show profiles, accessories, location, and dimensions.

C.	Samples: Manufacturer to provide upon request; sized to represent material adequately.

D.	Contract Closeout: Smoke vent manufacturer shall provide the manufacturer’s Warranty prior to the contract closeout [if applicable].

1.04		PRODUCT HANDLING

A.	All materials shall be delivered in manufacturer’s original packaging.

B.	Store materials in a dry, protected, well-vented area. The contractor shall thoroughly inspect product upon receipt and report damaged material immediately to delivering carrier and note such damage on the carrier’s freight bill of lading.

C.	Remove protective wrapping immediately after installation [if applicable].

1.05		SUBSTITUTIONS

A.	Proposals for substitution products shall be accepted only from bidding contractors and not less than (10) working days before bid due date. Contractor guarantees that proposed substitution shall meet the performance and quality standards of this specification.

1.06		JOB CONDITIONS

A.	Verify that other trades with related work are complete before installing smoke vent(s).

B.	Mounting surfaces shall be straight and secure; substrates shall be of proper width.

C.	Refer to the construction documents, shop drawings, and manufacturer’s installation instructions.

D.	Coordinate installation with roof membrane and roof insulation manufacturer’s instructions before starting.

E.	Observe all appropriate OSHA safety guidelines for this work.

1.07		WARRANTY/GUARANTEE

A.	Manufacturer’s standard warranty: Materials shall be free of defects in material and workmanship for a period of two years from the date of purchase. (10 years for the thermoformed plastic products) Should a part fail to function in normal use within this period, manufacturer shall furnish a new part at no charge. Special finishes, and other special equipment (if applicable) shall be warranted separately by the manufacturers of those products.

II. 		PART TWO - PRODUCTS

2.01		MANUFACTURER

A.	Bilco UK, 20 Park Farm Business Centre, Fornham St Genevieve, Bury St Edmunds, Suffolk, IP28 6TS.

Tel. 01284 701696. Fax. 01284 702531, Web: www.bilcouk.com

2.02		SMOKE VENT

A.	Furnish and install where indicated on plans smoke vent Type SKY-1M, size width: 1000mm x length: 1500mm. The smoke vent shall be single leaf and provide 1.0m² clear vent area. The smoke vent shall be pre-assembled from the manufacturer.

B. 	Performance characteristics:

1.		Dome has been tested for impact resistance to EN1873 Class SB1200

2.      Security glass classified 2(B)2 according to EB 12600:2004

3.		Operation of the cover shall be through a 24VDC power supply.

4.		Operation of the cover shall not be affected by temperature.

5.		Entire hatch shall be weathertight.

6.		`u` value 1.02 W/m²K

C.	Cover: Shall be a double-layer thermoformed polycarbonate dome assembled on a fully welded PVC frame, in which a double-layer security glass shall be inserted. Cover shall have extruded EPDM rubber gasket to ensure a continuous seal when compressed in the front and in the back of the vent.

D.	Cover insulation: not applicable.

E.	Curb: Shall be 250mm in height and of double-layer (internal and external) polyester resin reinforced with fiberglass. The curb shall be formed with a 150mm flange with 9mm holes provided for securing to the roof deck.

F.  Wind Deflectors: not provided.

G.	Curb insulation: Shall be extruded polyurethane of 60mm thickness

H.		Operating mechanism -  a single rotating actuator mounted on a sliding carriage capable of opening the cover to the fire open position of 180 degrees. ( note – roof obstructions should be considered )

I.  Finishes: Factory finish shall be:

- Polycarbonate: clear finish

- Glass: clear finish

- Pvc profiles: white

- Metal profiles: white powder coating

- Upstand: white

2.03		PERFORMANCE TO EN12101-2

Free Aerodynamic area 		1.01m²

Reliability 			RE 2000 (double function*)

Snow Load   			SL 500

Low Ambient Temp		T (00)

Wind Load			WL 1500

Resistance to Heat		B 300

*can be used also as a day to day ventilator.

III. 		PART THREE - EXECUTION

3.01		INSPECTION

A.		Verify that smoke vent installation will not disrupt other trades. Verify that the substrate is dry, clean, and free of foreign matter. Report and correct defects prior to any installation.

3.02 	INSTALLATION

A.		Submit product design drawings for review and approval to the architect or specifier before fabrication.

B.		The installer shall check as-built conditions and verify the manufacturer’s smoke vent details for accuracy to fit the application prior to fabrication. The installer shall comply with the smoke vent Manufacturer's installation instructions.

C.		The installer shall furnish mechanical fasteners consistent with the roof requirements.

01/10/16